## Art & Art History
Art and Art History
Rank | Priority | Work Order # | Area/Building/Room# | Issue | As of 10/6/2016 | As of 3/23/2017 | As of 3/27/2017 | As of 10/20/17 | SFA/Facilities Update as of 11/01/18 | SFA Facility Issues as of 11/16/2018 | SFA Facilities Update as of 3/7/2019 | SFA Facilities Update as of 04/18/2019 | Progress
1 | S | 726362, 729871 | Art Building Studio Spaces | Electrical wall outlets are short circuiting: Walls that share an outlet are subject to short-circuiting. Example: plugging in a movable light for a model in AB 113 and plugging in lighting on the other side (AB 112) causes a short circuit | Building is maxed out. Could we possibly integrate new electrical system within infrastructure on production facility? | New and/or upgrade of electrical system is not feasible at this time. Colleen recommends that a project proposal should at least be prepared to evaluate and assess scope, timeline and cost. 5 Yr Plan | Lighting: a comprehensive list of all lighting issues is included in a separate document. This list contains the same issues and concerns that were generated by a walkthrough that occurred in fall 2016, that is not yet resolved. | FacOps is aware of classroom lighting issue and is slowly working to address. Colleen to followup with Cora Lynn and Jay to evaluate progress based upon Arts issue list | All rooms have been replaced with new LED lights. Room 109 continues to be an issue. Track lights may be incompatible with new LED ~ to be addressed with J. Johnston | Needs resolution to room 109 | Needs resolution to room 109 | Needs resolution to room 109
2 | S |  | Art Ceramic Studio Ventilation | Environmental Health and Safety has cited ventilation issues again. We are working with them to rectify this but it is an ongoing issue. |  | Project approved, occurring over summer 2017 | Scott Ballo UPDC | Nickie Bock reports the project is complete and functioning beautifully. 10/2017
2 | ILT |  | Bishop Print shop | Temperature Control is Non-existent: Large Print shop space (#2), Letterpress Space (#3), and Silkscreen Lab (#12): Temperatures are far too cold, summer through winter. There’s no local control of the temperature in any of the printmaking spaces. DMD spaces share this issue (though their rooms are too hot- ours are too cold). It is difficult to work in this otherwise useful space, and this space is used daily by Art and Art History students and faculty. | See notes on HVAC concerns within DMD |  | John & Laurie have reported this OK | Laurie Sloan reports this is largely resolved in the Printshop spaces (cannot speak for DM). | Completed; closed-out | Completed; closed-out | Completed; closed-out | Completed; closed-out
3 | ILT |  | Art Building Classroom Heating Units | Should be functioning before winter. In the process of being converted from a pneumatic system to electrical? Otherwise, units are extremely loud, and entirely disruptive to use during class. Units are often turned off simply to be able to have class lectures and critiques. Students work, instead, in coats, hats, and scarves. | Jay & Cora Lynn completed walkthrough to review classrooms affected. Jay completed W/O’s to have these rooms fixed. | (Cora Lynn) Heating Units in ARTB #108, 111, 112, 113: the usual issues remain- the units are so loud when running that faculty routinely choose to turn them off in order to deliver lecture material or conduct critiques. You cannot, otherwise, hear anything. When the units are running the noise is considerable but students can at least be more comfortable. In order to hear, though, students must bundle up to work. This is unacceptable. | Dave Garside – switch install rooms 108 111 112 113 heating units- switch lower so step stool isn’t needed | Thermostats should be moved lower for access. If possible, replace these units completely. The same issues remain. Poor temperature control and impossibly noisy to hold class if the units are running. Rm. 109 is unbearably hot. Back doors cannot be opened without moving out the huge partitions. Circulation is achieved by turning up the thermostat (so it thinks we want the room warmer). As long as the heat is not on that will circulate air, but with no cooling or de-humidifying. Fall classes have been unbearable. M. Bock reports that #116 NEW system was apparently continually breaking down last spring. Not sure where that stands now. Colleen inquired if units can be replaced with remote thermostats. Eric Kruger to evaluate, Colleen to follow up. | Unresolved; need update from Facilities. | Unresolved; need update from Facilities. | Unresolved; need update from Facilities. | Unresolved; need update from Facilities.
4 | ILT |  | Bishop Print shop | Rusty Water Issue: Rusty water in paper soaking sink. Paper in the paper soaking sink turns brown on the edges. Instructors bring in water from home for some projects including all visiting artist projects. This is unacceptable for a working print shop. | Facilities believes this was resolved with a new filter. Cora Lynn will check with Laurie Sloan to confirm it is no longer a concern. -continuously rusty discolored RO unit | Filter has been installed. Will need to be replaced due to the nature of use. Place work order when replacement filter is needed. | Dave Garside- rusty water Bishop CT water to do evaluation | This issue remains- turns paper brown. The filter has not worked. Colleen to follow up with Jay | Unresolved; need update from Facilities. | Unresolved; need update from Facilities. | Unresolved; need update from Facilities. | Unresolved; need update from Facilities.
5 | ILT |  | Bishop | Leaking Ceiling across Multiple Rooms (some with hi-tech equipment): May begin to drip again- bowing as we speak. The Roof Leaks continuously. The leaks often come through the light fixtures, forcing us to turn off that row of lights. Leaks through the tiles ruins tiles and threatens expensive cameras. Covering the stop-motion work spaces will not work (will ruin the shot). | Restoration of patching/sealing has concluded. New individual leaks will be addressed with new w/o | Update 3.24 (Cora Lynn) Though this is ongoing from prior reports, there are new leaks in the ceiling. The decision has been made to not report the new leaks to Facilities. They are in the hallway and remedied by bucket placement. Plugging up the leaks only results in leaks in new areas. We have determined the devil we know (hallway) is better than the devil we don’t (unknown location of new leaks- possibly over irreplaceable technological equipment) |  | This situation is ongoing and worsening. See separate account (additional document). Carissa will send to Eric K., Jay Dave K. Patching has been completed. Recommend to pls. continue to report leaks to create document of issues | Unresolved; still in progress. Patching and repairing in place until Bishop roof replacement occurs. Continue to report leaks and document issues. Close-out on Facilities Issues Document; Bishop Center roof replacement converted to a UPDC project. Per Aug 2018 meeting with UPDC (M. Groza), roof to be replaced summer 2020; current scope includes replacement of roof membrane and replacement of HVAC/mechanicals. | Roof project on hold indefinitely. UPDC to confirm latest timeline. | Roof project on hold indefinitely. UPDC to confirm latest timeline. | Roof project on hold indefinitely. UPDC to confirm latest timeline.
6 | ILT |  | Bishop, 2nd floor | Excessive Noise, Central Air Unit/Mechanicals on Roof: Central air unit is noisy: constant continuous hum. Place sound attenuators on the vents on the roof? This is a top issue - people can't concentrate to work, communicate or hear presentations/films/crits unless this noise can be reduced. At the very least – find out which specific elements are causing the noise - ventilation, air conditioning, heating, other electrical systems. Maybe the sound can be dampened before replacing the roof begins (which could be some time out). Continual noise at this level may be injurious to students and employees. | See notes on roof replacement within Bishop |  |  | Also ongoing - see additional document. Carissa will send to facilities. There are blue items that appear to dampen noise. | Unresolved; still in progress. Excessive noise will continue until Bishop roof/mechanical replacement occurs. Update 11/01/18: Continue to report and document issues. Close-out on Facilities Issues Document; Bishop Center converted to a UPDC project. Per Aug 2018 meeting with UPDC (M. Groza), roof to be replaced summer 2020; current scope includes replacement of roof membrane and replacement of HVAC/mechanicals. | Roof project on hold indefinitely. UPDC to confirm latest timeline. | Roof project on hold indefinitely. UPDC to confirm latest timeline. | Roof project on hold indefinitely. UPDC to confirm latest timeline.
7 | ILT |  | Art Ceramic Studio | Water Seepage during Rain: Regrading needed around building to stop water flow into first floor when it rains. This problem was corrected at McMann but neglected at ACS. | Still an issue Rick talked to Bob Fl. Will regrade area |  | Grading outside and Bob Flowers | Eric K talked to Bob Flowers about re-grading area to reduce water flow into 1st floor. | Unresolved; need update from Facilities. | Unresolved; need update from Facilities. | Unresolved; need update from Facilities. | Unresolved; need update from Facilities.
8 |  |  | Art Ceramic Studio | Landscaping |  |  |  | Landscaping, Broken Asphalt and Litter around the building continues to be a huge problem. The poison ivy by the back entrance has been kept under better control, but everywhere else around the perimeter is a dump. The new fence around the transformers on the south side of ACS prevents mowing or weed control, & the loose gravel is washing away to great ruts where the steam pipes had to be dug up a couple of year ago. I notice large stone gravel has replaced unmanageable grassy area by the roadside leading to McMann & ACS. Replacing all the weedy dirt around the parameter base of ACS would be a good solution. We’ve also never been able to count on daily litter pick up around the building, no matter how often we request it. Enter WO to remove poison ivy, Aris manages greenspaces | Unresolved; need update from Facilities. | Unresolved; need update from Facilities. | Unresolved; need update from Facilities. | Unresolved; need update from Facilities.
9 |  |  | Art Ceramic Studio | Handicap Access |  |  |  | Lack of handicap access to second floor is a major code violation. Interior is the issue, Meet with Dave Koehler Colleen to reach out to Donna Korbel in ADA compliancy. Possible create project request | Unresolved; C. Bridgeman entered Project Request as of 02/19/18. Update 10/4/18 - Close-out on Facilities Issues Document; a site visit to the building by UPDC confirms a combination of factors are restricting renovations and further indicates that committee members decided improvements to this building would be cost prohibitive to warrant a project at this time. These factors include but are not limited to: (1) deferred maintenance repairs are required for the building, (2) significant exterior grading for a compliant sidewalk approach is necessary, (3) required exit egress, (4) ground level provides accessibility to first floor teaching space--department should determine if handicap need is warranted. | Project closed out; see 11/01/18 notes. | Project closed out; see 11/01/18 notes. | Project closed out; see 11/01/18 notes.
10 |  |  | Art Ceramic Studio | Exterior framing & siding |  |  |  | Looks much better since the paint job, but the rotting wood particularly where dirt and leaves pile up around the foundation is defeating the new paint job. | Unresolved; need update from Facilities. | Unresolved; need update from Facilities. | Unresolved; need update from Facilities. | Unresolved; need update from Facilities.
11 |  |  | Art Ceramic Studio | Damp Room - Peeling paint is being evaluated for lead content. Depending on results, work order is in place for appropriate patcing and repainting of damp room over winter term. |  |  |  | Currently being address by Jon Cooke & the paint shop. | Unresolved; need update from Facilities. | Unresolved; need update from Facilities. | Unresolved; need update from Facilities. | Unresolved; need update from Facilities.
12 | ILT |  | Art Building, Rm 105 Leaking Ceiling | HVAC people had ordered the parts to permanently correct the situation. The parts are supposed to be in the mechanical room on the second floor but are not installed? On 4/7/2016 (based on recent walkthrough): Work has been going on in the Mechanical Room. What have they done to fix the leaks? The ceiling MUST go. Damaged beyond damaged. | This classroom will be submitted to the Classroom Committee for upgrades. Leaking from the mechanical room. Water around the floor, drain is rotted out – matches ceiling tile. W/O has been closed, Jay will find out if there is a plan to fix it | Has this been submitted to the Classroom Renovation Committee? Can only use this room as storage in its present state. Needs: re-lamping, leaking ceiling fixed, new carpet (or no carpet), paint, new ceiling. Equipment/furnishings needed: Tables & chairs; Enlarger; Trimmer; Lockable cabinets; Shelving |  | Leak is fixed: Jay will work with Pete to fix/replace all items to have classroom functional before semester begins. Additional time will be needed to move pianos to this room before 1st day of classes Colleen to follow up with Cora Lynn regarding moving logistics plan | J. Johnston coordinating with T. Haskell regarding move out. Jay will coordinate renovations. Water penetration in space should be rectified before renovations begin. Renovations to include: replacement of ceiling tiles as necessary, painting and installation of floor elecrtrical outlets for electric pianos/keyboards. Update 11/01/18: Close-out on Facilities Issues Document - project complete. | Project completed; closed out. See 11/01/18 notes. | Project completed; closed out. See 11/01/18 notes. | Project completed; closed out. See 11/01/18 notes.
13 | O |  | Contemporary Arts Gallery | Track lighting is finicky and ancient. CAG needs a new ceiling (an open metal grid). Facilities estimated (last summer, 2014? 2015?) $9,000 would cover the cost of an attractive ceiling grid, some new track lighting and moving the light switches into the CAG. Currently David Koehler is our contact. |  | This is a public space. Derek and Peter will look into this memo |  | Project Request Form will be submitted See additional document for details regarding CAG space. *Colleen to enter project request | Unresolved; C. Bridgeman entered Project Request as of 02/19/18. Update 11/07/18 - per DH, J. Richardson, gallery received new LED lights, a drop ceiling and curtains. This need can be removed from the deferred maintenance list. | Project completed; closed out. See 11/01/18 notes. | Project completed; closed out. See 11/01/18 notes. | Project completed; closed out. See 11/01/18 notes.
14 |  |  | Art Building RM 101 | This room is either too hot (even in winter) or too cold, with the humidity constantly changing. Occupants attempt to regulate temperature by opening the exterior door, which leaves the space too dirty (dead leaves, etc.) to be used as a clean room for photograpy. |  | Art will place without and Dave will follow up -102 and 103 split system |  | Split HVAC units have been installed in 102 & 103 Cleaning staff have been given access from AAH to clean rooms Ceiling tiles damaged during installation (in the new hallway/lobby ceiling) have not been repaired/replaced. A work order went in immediately, near the beginning of the semester. Eric K to follow up | Unresolved; need update from Facilities. | Unresolved; need update from Facilities. | Unresolved; need update from Facilities. | Unresolved; need update from Facilities.
15 |  |  | DRMU building | Photography Darkroom: ventilation is inefficient and unstable |  | Can have it evaluated, fluff/buff DRMU - JUNE 15TH | FacOps can have it evaluated during DRMU ceiling renovation | See additional document for details regarding Darkroom space. Colleen to enter project request. Please communicate with Janet Prichard & Dan Buttrey for dark room needs | Unresolved; C. Bridgeman entered Project Request as of 02/19/18. Update 11/01/18: In progress - project scope is being prepared by Department Head; further review with COO and Academic Renovations once requirements are vetted. | Unresolved; need update from Facilities. | Unresolved; need update from Facilities. | FacOps has agreed to a revised renovation summer 2019 schedule inclusive of: (1) minor modifications(partially remove interior partition in 115B) to the advanced lab area to accommodate a longer/deeper sink, (2) plumbing repair to address pressure and temperature issues, (3) secure dividers on workstations in advanced lab, (4) replace door seals to film processing rooms, (5) evaluate HVAC reliability and adequacy, (6) relocate eyewash shower closer to front of room, (6) paint room 115.
16 |  |  | Punch list from summer renovation | a. Door painting- needs to be gray b. Hall gallery- rubber tile replacement c. Lighting for gallery walls, specs called for 6, each bay only has 4 installed d. Missing cable locks replacement e. Exposed wires need to be tidied up |  |  |  | Doors have been painted but not the frames. Carissa entered another work order per FacOps request to complete frames, not yet complete Additional heads were installed in the hallway gallery bays- this is positive. They do not match the original heads and, therefore, give off a different color light than the existing heads. This is not positive. Someone came to work on the exposed wires today (10/17). Results unknown. Rubber tile replacement has not taken place. Colleen to work with Dave Koehler to address | Update 11/01/18: Door frames painted/complete. Still need rubber tile replaced for Hall Gallery space; C. Bridgeman to have further follow-up is needed with Dave Koehler. | Unresolved; need update from Facilities. | Unresolved; need update from Facilities. | Unresolved; need update from Facilities.
17 |  |  | All Art Buildings | Inconistent cleaning |  |  |  | Art 118: Sink needs to be professionally cleaned. Art 119: Sink needs to be professionally cleaned. Special w/o needed because of chemicals to clean sink Art 120: Needs soap dispenser and sometime damp mopping (once per week, as per ceramics lab). Should be regularly stocked with paper towels. Colleen to discuss with Jay—should we enter WO for additional custodial requests? | Unresolved; need update from Facilities. | Unresolved; need update from Facilities. | Unresolved; need update from Facilities. | Unresolved; need update from Facilities.
18 |  |  | ART 105 | Water intrusion originating in Mechanical Room above space. Piano lab is moving back into this space during the Winter Session and concerned about continual leaks to the space, restitution for items lost and the accessibility of the space going forward. | [5 empty] | Additionally, ruining some sheet music and perhaps damage to electric pianos; Facilities has plans to epoxy the floor in the Mechanical Room above. Facilities to put on radar. | Jay to confirm--Waterproofing to begin during spring break week. | Waterproofing complete.
19 |  |  | Art Building | Art Building HVAC; Not all of the air handlers on the roof are working and the air intake has been diminished to lower the fan noise, however CO2 monitors and measurements are not working correctly. Thermostats are also inoperable. | [5 empty] | There is an upcoming roof project occurring this summer; however in the interim, Facilities will look at the air intake with regards to CO2 and revisit the thermostats. | Meeting with DH and HVAC in progress. | per 2/19 meeting with DH and Facilities, HVAC mechanicals will continued to be maintained and not replaced as part of the roof project scheduled for summer 2019.

## Dramatic Arts
Dramatic Arts
Rank | Priority | Work Order # | Area/Building/Room# | Issue | As of 10/6/2016 | As of 3/23/2017 | As of 3/27/2017 | As of 10/20/17 | SFA Facility Issues as of 11/16/2018 | SFA Facilities Update as of 3/7/2019 | SFA Facilities Update as of 04/18/2019 | Progress
1 | ILT | 699951 708714 721905 729748 730599 | Katter Theatre, 1st floor acting studios | Outstanding HVAC issues | This has been investigated and there are barriers to resolving HVAC problems. Eric Krueger will be in contact with Pete Mcqueeney on status and touch base accordingly. |  | HVAC- exchange installed on 3/24 Michael Bradford will follow up to confirm it is working properly | Completed
1 | ILT |  | HSJ Theater | Energy Consultation & Theatrical Lighting Upgrade | Mike Demers, stage electrician, has been researching this. Been in touch with Stan Nolen. Will work to incorporate all performing areas into a grant. Will also connect with Kirk Matson regarding writing grant for replacement lighting. Could be pushed to UPDC depending on scope. Cost benefit analysis will need to be completed. 60% would be rebate | Mike has toured ECSU's theaters and recital hall where they have many of these LED fixtures currently installed. -LED concerns- the lights contains fans, so they make noise. Mike was able to find that the fans are on thermostats and even then they can be overridden by the controls in the control room. -Sara Willey, a sales rep with Barbizon lighting, has been invited to come to the Katter theater to give a LED demo. Current fixtures will be hung so group can look at them in a "shootout" manner. All areas will be attend to ensure LEDs will work for their space. The demo date should be solidified within a week. |  | Project is ongoing-- funding is the issue Established that light from LED noise wouldn’t impact performances Mike Demers-applying for Eversource grant to pay for the upgrade |  |  | Mike D. is in progress of completing an updated engineering study, which would require the following information compiled: 1) the installation cost for each location of the equipment we wish to purchase 2) Number, wattage and type of existing fixtures use (on average) for each location 3) Number of operating hours a year for existing fixtures at each location 4) Number, wattage and type of new fixtures for each new location Follow up meetings with: Energy Management, Capital Budget & Planning and Provost Office are required once study is complete and cost benefit is reevaluated.
2 |  |  | HSJ Theater | Trap Room Water Project | Directly below theatre stage, groundwater is seeping into this area and waterproofing upgrades are needed to ensure water is sent to an area it can be pumped out of the building. A pipe was hit during attempt to remedy the initial issue |  | A design firm has been hired to engineer solution. With CRT summer season soon underway and the stage also being needed for Fall productions, project must be completed within the summer break or held off depending on length anticipated for the project. Hole doesn’t compromise integrity structure, install pumps 30 days (roof drain has been unclogged) | Work began on10/16 to remove 3 upstage traps to allow access into trap room. Project will take 6-8 weeks to complete. Drama will need assistance to moving materials into trap room and relocating materials once the project is completed. Storage units will be funded by DRU Piping repairs with mechanical contractor. Nov will be floor portion | Renovation in progress | Renovation in progress | Project complete and shelving installed. Close out with Facilities.
3 | S |  | Jorgensen Costume Shop | 2nd industrial dehumidifier died last summer and been replaced with a wall hookup. | This will be a major concern with upcoming summer and 2nd industrial dehumidifier is crucial to handle moisture output, mold has resulted in past. |  | An air quality assessment was put into w/o (M720872) but closed as they determined the A/C was working without a test being completed. | Costume Stock Room has been renovated: Flooring has been abated and replaced. De-humidifier has now plumbed to wall drain. Costumes are being dry-cleaned and treated by Battison’s. They’re being returned weekly as dry cleaning is completed. | Project complete. Close out w/ Facilities. | Project complete. Close out w/ Facilities. | Project complete. Close out w/ Facilities.
4 | ITL |  | DRMU 101 | Shades | Appropriate shades needed on West windows so that classes are not blinded by the afternoon sun and will also block afternoon heat |  | Enter WO's to have shades repaired | Not installed yet | Issue rectified. Close out w/ Facilities. | Issue rectified. Close out w/ Facilities. | Issue rectified. Close out w/ Facilities.
5 | ITL | M765887 | DRMU 109 | Shades | Shades fell down and were not reinstalled |  |  | Blinds are reinstalled, are light and allow too much sun into the classroom which disrupts use of smart board projector Enter WO for blackout shade install | Need update from Dramatic Arts to see if issue has been rectified. | Need update from Dramatic Arts to see if issue has been rectified. | Need update from Dramatic Arts to see if issue has been rectified.
6 | ITL |  | DRMU Building | Ceiling | Ceiling and lighting has been replaced in hallways |  |  | Areas with popcorn ceilings were not part of the renovation. Can completion be incorporated into Winter Intersession or during the MUS renovation in Summer 2018 *Colleen to follow up with Sunnie | Project on hold indefinitely. Need update from Facilities to understand when this will be rescheduled. | Project on hold indefinitely. Need update from Facilities to understand when this will be rescheduled. | Project on hold indefinitely. Need update from Facilities to understand when this will be rescheduled.
7 | A, IPE |  | Nafe Katter Theatre | Lobby |  |  |  | Flooding occurs in the lobby when rain storms occur; grading outside allows water to pool and flood; concern that mold will occur from the repetitive flooding: Colleen to request EHS complete a mold assessment of the lobby. Part of deferred maintenance project list. Lawn needs draining to prevent flooding *Colleen to follow up | Issue rectified; project complete. Close out w/ Facilities. | Issue rectified; project complete. Close out w/ Facilities. | Issue rectified; project complete. Close out w/ Facilities.
8 | S, IPE |  | HSJ Theater | Lobby |  |  |  | Flooring Replacement & repainting needed, Colleen, Pete, Jay , Eric will walk through to assess the scope of project asbestos floor. Lobby is free between Nov-April *Colleen to follow up with Jay | Project on hold indefinitely. Need update from Facilities to understand when this will be rescheduled. | Project on hold indefinitely. Need update from Facilities to understand when this will be rescheduled. | Project on hold indefinitely. Need update from Facilities to understand when this will be rescheduled.
9 | ITL | M771313 | DRMU 128 | A/C Units |  |  |  | Roll away units requested, similar to work in 228. No power in classroom for window-wall hookup. In the case of classroom 128, Drama would be responsible for $1200, facilities would cover the cost remaining of installing the split-system*. This would include getting electrical power to that side of the room. (* per HVAC, roll-away may not be ideal for this room, a split-system may be more efficient.) | Project has been transferred to UPDC within Fine Arts Phase II project. Split unit system to be installed and will provide conditioning to the following rooms: DRMU 128, 227 and 228. | Project has been transferred to UPDC within Fine Arts Phase II project. Split unit system to be installed and will provide conditioning to the following rooms: DRMU 128, 227 and 228. | Project has been transferred to UPDC within Fine Arts Phase II project. Split unit system to be installed and will provide conditioning to the following rooms: DRMU 128, 227 and 228.
10 |  |  | Department Storage |  |  |  |  | Maria Groza- showed 3 spaces on depot campus near ball field for storage in Nafe Katter near Production Facility | Temp storage provided on Depot Campus. Items will be relocated once Production Facility is completed. | N/A | N/A
11 |  |  | Nafe Katter & Studio Theatre | Handicap accessible gender neutral bathrooms |  |  |  | Project Request Form for this project. Converting bathrooms within red hallway - will need to confirm all measurements for ADA compliance. Might be a good opportunity to incoporate a lactation room. | Follow up needed w/ Drama -- these bathrooms have multiple bathroom stalls. | N/A | N/A
12 |  |  | Studio Theatre | Hallway lighting |  |  |  | Dimming is needed for performances. Will need fire marshal agreement for code and egress requirements (Jay will help with this), Dimming could be controlled through Bluetooth option for safety Colleen to follow up Eric K suggested dimming system could be way to add remote controlled LED lights vs wall switches. Add WO after building inspector signs off | N/A | N/A | Issue not rectified; issue needs follow up with Drama and Facilities
13 | S |  | Studio Theatre | Main doors to the Theatre do not lock. Newly renovated double doors. |  |  |  |  | On-Going; Facilities noted this issue has been over-looked. They have placed a new work order and indicated this as a security concern. Facilities will have a locksmith over today to see what can be rattified. | OK; Complete per B.Copley | Issue rectified; project complete. Close out w/ Facilities.
14 | S |  | Nafe Katter Theatre | Landing step leading to the Katter Lobby has peeling rubber that needs to be replaced. Work order has been placed regarding this issue. |  |  |  |  | New item; work order placed. Facilities to follow up. | Colleen brought Jay to tripping hazard area of the Nafe Katter; Jay to follow-up | Need update from Facilities to see if issue has been rectified.
15 | ITL |  | Trap Doors and Trap Space | [6 empty] | Per Jay, need to know if vendor provided sketch is sufficient for installation and permit; need to determine who will install. Jay to follow-up with Glen Mathieu and Mickey Gorman | Issue rectified; project complete. Close out w/ Facilities.

## Music
Music
Rank | Priority | Work Order Number | Area/Building/Room# | Issue | As of 10/6/2016 | As of 3/23/2017 | As of 3/27/2017 | As of 10/20/17 | SFA/Facilities Update as of 11/01/18 | SFA Facility Issues as of 11/16/2018 | SFA Facilities Update as of 3/7/2019 | Progress
1 | S |  | Music Basement | Security cameras needed in remote spaces - Window cutouts needed for studio doors - Help call button -Any future projects to be incorporated with security -Any new camera installed or renewed has to be OK’d with Chief of Police | Andrew Langlais is point of contact within UConn police. Colleen will meet with him to assess basement security and work on resolution. Colleen and Dr. Rice met with Andrew Langlais to review security concerns for the Music Basement in the fall. Status update and assessment report requested; TBD. |  | Colleen will follow up with Andrew Langlais regarding Music basement Eric Rice- music storage tour through post commencement | Andrew Langlais is no longer with the University. Eric Rice needs to address with Hans Rhynhart and Mike McCue, cc: Eric Kruger, Colleen B MLIB basement Orchestra Band basement; area is basically sound proof with many hidden corners and is a security nightmare | C. Bridgeman in discussion with Detective Hanna; requesting a security assessment of identified space and mitigation plan. | There are currently no windows or cameras in this space. It does not feel safe or secure. Would like to discuss additional lighting or security cameras. Contact Detective Hanna to have him tour the space and provide a security assessment. | CKB to follow up w/ Public Safety/Emergency Management.
2 | S & A |  | Music, back entrance | Facing von der Mehden, Overhang & soffit upgrades |  | Soffits will not be replaced until façade project is completed. Colleen would like safety assessment completed by engineer to ensure that they are of sound and will not collapse before façade project is completed. Front overhang facing 195 should also be assessed for safety integrity concerns. | Soffits - Eric Kruger committed to have staging installed on all soffits – will send engineer to have evaluated. - New Business: in vdm, concrete overhangs are crumbling. Kirk can see rebar | Eric Kruger put on list. Not in façade project vdM overhang is not part of resolution either | Unresolved; need update from Facilities. | Unresolved; need update from Facilities. | Unresolved; need update from Facilities.
3 | S & ILT |  | Music Ensemble Rooms/ von der Mehden | Storage capacity for instruments and/or partition capability to easily access or store away instruments. vdM- storage capacity is inaccessible w/o ladder. Safety concerns for removing & adding instruments to storage in this location |  | goal is to do for design for summer Walk through will be coordinated with Eric Kruger, Colleen Bridgeman, Eric Rice and Maria Groza. Will add to po castle (vdm contractor) | -Eric Rice & Maria Groza will have tour current music storage after commencement | Will include into large meeting with Anne & Maria | Unresolved; C. Bridgeman scheduling meeting with M. Groza | Unresolved; C. Bridgeman scheduling meeting with M. Groza | Unresolved; C. Bridgeman scheduling meeting with M. Groza
4 | ILT |  | Ensemble Rooms | Jaffe Holden Report- upgrade of sound dampening drapery – major ensemble rooms In Progress – Project Request submitted; Dave Koehler in process of providing project cost and scope for acoustical/sound dampening resolution. |  | Progress has been minimal on project; timeline and scope still TBD. Resolution is critical for upcoming accreditation in 2018. This issue was sited on the last accreditation and cannot go unresolved again |  | Project is proceeding forward w/ Academic Renovations. Target timelines is winter intersession Out to bid Tuesday with contractor walkthrough 10/24 diff time of year, Dave is hoping that it will produce lower competitive bids | Completed; closed-out. | N/A | N/A
5 |  |  | Von der Mehden | Freight elevator project- potential hazard of 10.5” gap between the upstage edge of the lift car and the garage door to access the 1st floor. Lift is used frequently to transport 9’ Steinway (1200 pounds). If the piano is pushed too far upstage, a caster could run of the lift car and cause a “teeter totter” action and force the downstage edge of the piano to lift. If anything is between the header and piano, it would be crushed (a head or body part). Appears fixable with removable kick rails to be placed on the cars edges. Project Request form was submitted in February. |  |  | Otis visited vdM on 3.23.17 | Elevator is fixed. Project completed, cable jumped, heavy/swing - gate struck open. Stephanie Marks is Otis contact. | Completed; closed-out. | N/A | N/A
6 |  |  | Von der Mehden | Carpet replacement incomplete |  |  |  | Carpet replaced within lobby and auditorium- office area needs to be completed, which was a part of the PO. Colleen to follow up with Jay | Completed; part of vdM renovation project over the summer/winter 2018/2019.
7 |  |  | Von der mehden | HVAC within lobby is antiquated and doesn't work |  |  |  | HVAC Unit replaced within the auditorium- Confirmation of replacement of lobby units for Summer 2018 | Per Facilities: Lobby Units canceled ; per Mike Rochetti: we need to install some sound attenuators on the ducts leading to the 4 rooftop exhaust fans serving the main recital hall. The job would probably be under $20K. CKB to follow up. | Project on hold indefinitely; need update from Facilities | Project on hold indefinitely; need update from Facilities
8 |  |  | Music Building | Ceiling renovation was deferred |  |  |  | Ceiling & Lighting replacement- Confirmation of renovation for Summer 2018 | Per Facilities: A. Ristau working on this - Tom M is PM - schedule is for summer 2018; need update from Facilities | Project on hold indefinitely; need update from Facilities | Project on hold indefinitely; need update from Facilities
9 | S |  | Elevator outside MusB 102 | The floor indicator light is not working and the elevator is jerky in movement. | [5 empty] | In need of servicing as students utilize this elevator for transporting large instruments. | OK; Complete per E. Rice
10 | ITL |  | Music Buidling | Sound panels are missing from various locations in the Music Building; extra panels are stored in the dead file and harp rooms; need to determine where to install and cost | [5 empty] | Needs to identify space where panels should be installed and put in a subsequent work order. | per Eric Rice; someone from Facilities came and spoke to Jessye about the sound panels and getting them reattached
11 | ITL |  | Music Building; First Floor and Basement | Water Stained tiles | [5 empty] | There have been on-going work orders for this issue to see where the water is coming from. Facilities to follow up after work order placed. | OK; complete per E. Rice
12 | ITL |  | MusB 229 | Requesting card swipe access to this room as it is currently being used as a rehearsal space and classroom and is currently only accessible by key. | [5 empty] | May need to discuss replacement of door arrangement in order for card swipe access to work properly. Colleen wishes to take this discussion offline and speak with Dana about electronic access. | CKB to follow up with DH and discuss funding for this project.
13 | S |  | Von der mehden | Lift Issue. Gate to close and activate lift often is de-railed and the counterweight system needs to be looked at. OTIS has looked at this lift twice in the past five years. | [5 empty] | Facilities requests that a work order be made so they can follow up. | OK; complete per E. Rice

## Digital Media & Design
Digital Media and Design
Rank | Priority | Work Order Number | Area/Building/Room# | Issue | As of 10/6/2016 | As of 3/23/2017 | As of 3/27/2017 | As of 10/20/17 | SFA/Facilities Update as of 11/01/18 | SFA Facility Issues as of 11/16/2018 | SFA Facilities Update as of 3/7/2019 | Progress
1 | ILT |  | Bishop 2nd floor Cigna Room | Airflow and boiler room noise rendering the Cigna Innovation Lab space unusable for students and faculty. Is there a short-term fix to the noise prior to the roof replacement project? | Roof will have 300 sq. ft of restoration in Spring 2017. They will cut out and replace the bad section of the roof. They will work to find out the sound cause during replacement and work to mitigate the sound or resolve completely | Roof mechanicals have been tuned up. A sound/vibration consultant will be brought in to confirm if more can be done with noise. Send for contractor, there will be no HVAC or roof replacement | Continuation of painting effort in faculty offices |  | Unresolved; C. Bridgeman entered Project Request as of 02/19/18. Update: 11/01/18: Close-out on Facilities Issues Document; Bishop Center converted to a UPDC project. Per Aug 2018 meeting with UPDC (M. Groza), roof to be replaced summer 2020; current scope includes replacement of roof membrane and replacement of HVAC/mechanicals. | Roof project on hold indefinitely. UPDC to confirm latest timeline. | Roof project on hold indefinitely. UPDC to confirm latest timeline.
2 | ILT | 717982, 725215, 729951, 729659 | Bishop 146 007 005 | HVAC Issues: this semester we had a compressor failure for room 146 that lasted a few weeks during the beginning of the semester. After that was fixed, we lost AC in room 007 (which has computers and no windows and gets very hot). Next, we lost AC in room 005, then the hallway in the basement last week and during open house this weekend. Now no AC on the 2nd floor. | HVAC cannot be replaced. Would need at least 6 months to complete all new ductwork and zone control within building. Tony Weston will arrange meeting with Tim & engineers to discuss HVAC remedies. Colleen & Cora Lynn will also attend. |  | will get quote for split unit stabilized for now but it’s been cool Replacement of ceiling tiles in Rm 146; P. McQueeney will walk with Aris to review ceiling tiles issues in Bishop | Can we close? | TBD; Need to confirm with DMD if issues resolved. | TBD; Need to confirm with DMD if issues resolved. | TBD; Need to confirm with DMD if issues resolved.
3 | ILT |  | Bishop Basement | The 4-5 heat pumps located in the ceilings above the DMD hallway work space. These often leak and fail on a fairly regular basis requiring us to remove much of our equipment located in that hallway space in support of Facilities work on those pumps. |  | Basement pumps have been greased and updated. They will look to replace & change out with space renovation when completed on first floor |  | Can we close? | TBD; Need to confirm with DMD if issues resolved. | TBD; Need to confirm with DMD if issues resolved. | TBD; Need to confirm with DMD if issues resolved.
4 |  |  | Bishop 1st Floor Lobby | Needs painting |  |  | Can be completed during 1st floor renovation over summer 2018 |  | C. Bridgeman/J. Johnston to ensure that it is in the queue. Update 11/01/18: per D. Koehler renovation can be incorporated into 1st floor space expansion project. C. Bridgeman to follow up with Academic Renovations. |  | Issue rectified; project complete. Close out w/ Facilities.
5 |  |  | Bishop Bathroom | Bathroom lighting and stall don’t work |  |  | Place a WO with FacOps to have addresed | Completed? | TBD; Need to confirm with DMD if issues resolved. | TBD; Need to confirm with DMD if issues resolved. | TBD; Need to confirm with DMD if issues resolved.
6 |  |  | Bishop 146 | Replacement of ceiling tiles |  |  | Colleen will complete walkthrough with Aris to review ceiling tile concerns |  | C. Bridgeman performed walk-through of 146 with Aris Ristau during the spring 2018; Unresolved; need update from Facilities. | TBD; Need to confim w/ Facilities. | TBD; Need to confim w/ Facilities.
7 |  |  | Exterior | Bike Racks |  |  |  | Bike racks are needed- students are locking their bikes to inappropriate areas, ex: dumpsters | Unresolved; C. Bridgeman entered Project Request as of 02/19/18. Update: Project with UPDC/in progress. |  | CKB following up with UPDC. Location specified by DMD. Target summer 2019 for installation.
8 |  |  | Bishop | Request for cleaning of Air Vents | [5 empty] | DMD is requesting someone to come and look at this issue. Colleen has correspondence regarding this that she will forward to Facilities. | Issue rectified; project complete. Close out w/ Facilities.

## Jorgensen
Jorgensen
Rank | Priority | Work Order Number | Area/Building/Room# | Issue | As of 10/6/2016 | As of 3/23/2017 | As of 3/27/2017 | As of 10/20/17 | SFA/Facilities Update as of 11/01/18 | SFA Facility Issues as of 11/16/2018 | SFA Facilities Update as of 3/7/2019 | Progress
1 | S X |  | Front Patio-Hillside Road | Concrete breaking up. Real safety concern. They are planning to address these issues before winter | Rod has been in touch with Sonny. Discussed completing half at a time to maintain easement of entrance. Plan to replace before winter season | Completed |  |  |  | There are currently no windows or cameras in this space. It does not feel safe or secure. Would like to discuss additional lighting or security cameras. Contact Detective Hanna to have him tour the space and provide a security assessment. | CKB
2 | S | 708566 - Locksets | Exterior doors to Jorgensen Lobbies and CRT Lobby | Doors are drafty and noisy but more importantly getting old and difficult to operate. A real safety concern that they are difficult to open. FIRE HAZARD. 12 weeks, nicer chosen Install time unknown Eric will quote | Replacing the existing doors will require services from architect/engineer for design purposes, since doors aren’t standard and would need to be custom | Plan to replace door closers, hardware, & weather stripping for all exterior doors. Type of hardware and order timeline needs to be decided by Jorg/CRT | Exterior door nice hardware chosen, 12 weeks will install after summer season – Eric Kruger will find quote for install $ and time frame | Hardware has been installed on all doors to the Jorgensen and the doors have been painted. Completed Waiting on weather Stripping – will make it air tight
3 | S X | Mike Jed will check | Jorgensen Front Steps | Need repointing as does brick exterior of building-Need repointing as does brick exterior of building Leah lower lobby- water leaking | After summer season |  | Bob Flowers will prioritize repointing front steps | Steps have been repointed.
1 | S | 646389 | Jorgensen side, Exterior Lighting | Receive many complaints that it is difficult to see at night-Approaching and leaving the facility. Safety hazard | Landscape Architect will review.Could be included into NW Science Quad project. | Jorgensen patron fell as a result of poor lighting. Patron’s condition was very serious and was taken away in ambulance. Facilities will complete a lighting survey, and will review upgrading to LED lights | Spotlights on roof are LED. FacOps have identified 3 areas to install better lighting | Erick- plan to light up stairs & add new lighting to overhang Theatre spotlight – 1 was installed as a test If Rod is happy they’ll continue lighting, but will not go over Gant project w/ Eileen McHugh lighting isn’t part of scope of project | Completed; closed-out | N/A | N/A
2 | IPE |  | Jorgensen Stage lighting | Instruments are old and need to be replaced |  | Dave MacIntosh from Eversource will complete a replenishment study | Scope of project replacement qualifies for huge rebate- intensity of color is not there | Currently collaborating with the Dramatic Arts department on the Energy Consultation and theatrical lighting upgrade initiate. Also pursuing funding through GUF committee | Update as of 11-01-18 - project in progress with Mike Demers. Current status: (1) Reidentifying project requirements, scope and venues (2) Soliciting lighting evaluation and cost benefit analysis with vendor, (3) Facilitating discussions with Uconn's Energy Management/Facilities team regarding latest proposal and Eversource current rebate recovery program |  | Mike D. is in progress of completing an updated engineering study, which would require the following information compiled: 1) the installation cost for each location of the equipment we wish to purchase 2) Number, wattage and type of existing fixtures use (on average) for each location 3) Number of operating hours a year for existing fixtures at each location 4) Number, wattage and type of new fixtures for each new location Follow up meetings with: Energy Management, Capital Budget & Planning and Provost Office are required once study is complete and cost benefit is reevaluated.
3 | IPE |  | Jorgensen; Exterior Doors at North and West side of the building. | [6 empty] | When exterior doors were painted and had hard-ware replacement, weather stripping was removed from the doors. Weather stripping is requested to be replaced before Winter. Facilities will check in on this matter and believes the West Exterior Door recently had weather stripping replaced. | OK; complete per R. Rock
4 | HS |  | Jorgensen Trap Room | Dust Mitigation | [5 empty] | Send request to Jay Johnston regarding storage. | Project complete and shelving installed. Close out with Facilities.
5 | IPE |  | Jorgensen South East Stair Well | Leaking | [5 empty] | Should be buttoned up by Winter. | Jay to Follow Up
6 | SIPE |  | Jorgensen Fly Rail | Lighting Issues | [5 empty] | Please send emails to Facilities | Colleen to follow up with Ed.

## Benton
Benton
Rank | Priority | Area/Building/Room# | Issue | As of 10/6/2016 | As of 3/23/2017 | As of 3/27/2017 | As of 10/20/17 | SFA/Facilities Update as of 11/01/18 | SFA Facility Issues as of 11/16/2018 | SFA Facilities Update as of 3/7/2019 | Progress
1 | IPE | B-5 Mechanical Room | Wall waterproofing and floor drainage to better protect collection storage during pipe leaks. | Has a history of repetitive leaks Creating curtain drains/cutting a groove in concrete could mitigate draining issues | Peter McQueeney to complete evaluation on 3.24 | Pete Mcqueeney/FacOps will replace a condensate pipe to prevent leaking | Can we close? Resolved per Nancy, Pete McQueeney is checking | Completed; closed-out. | N/A | N/A
2 | IPE | G-23 Mechanical Room | Leaky pressure relief valve possibly from waterlogged expansion tank. | Mechanical equipment or piping Resolved. Changed relief valve |  | Resolved. Changed relief valve | Completed
2 | IPE | All areas | Continued routine maintenance on HVAC systems especially units that affect galleries and collection storage | Gilman has been at 50% humidity-Rachel/John can confirm, not fully mitigated | Humidifier for Gilman Gallery is in quoting process |  | Still an ongoing issue. Not always at 50% humidity | Unresolved; need update from Facilities. |  | TBD; need to confirm with the Benton that issue has been rectified. HVAC SOP has been developed to ensure proper workflow and museum best practices and standard operating procedures are being followed.
3 | IPE | Parking lot/dock | Loading dock and parking area has become a garbage dump central for all neighboring buildings | Aris to check in with Bob Flowers to see if vertipack machines can be used in place of current dumpster |  | Aris to check with Bob Flowers to see if new vertipacks can be coordinated with new patio at the Benton | Reduced # of cans. Aris explored compactor but electricity associated posed financial challenges. Nancy seems to notice an improvement and it’s been cleaner | Completed; closed-out. | N/A | N/A
4 |  | Gallery | Light switches -will need to crnfinuty poof LED’s, Nancy will purchase. -Contrary to do reimbursement | Eric Krueger addressed light switch transition to one breaker that has matching switch plates and dimmers. | Goal is to have computerized electrical panel—possibly Summer 2017 | Nancy and Kerry – will confirm type of LED’s to Benton needs. Eric Krueger will check on reimbursement for previously purchased LED lights | Some don’t work/ switches overall need to be upgraded and uniformed. Computerized electrical panel needs to be implemented. Not clear on “Action Item’. Follow up with Eric K. Nancy needs assistance w/ electric shop to install; have had them for 2 years. Light switches can’t be done in house. | Unresolved; need update from Facilities. | Unresolved; need update from Facilities. | Unresolved; need update from Facilities.
5 | S, IPE | Benton Museum | Specialized security needed for galleries. Project Request Form completed. Coordinating security consultants from museums through Chuck Brome. | Awaiting sign off on vendors and wil request proposals for security system installation |  | Eric Kruger will work with Chuck Brome to coordinate security for Benton and light switches | Colleen attended conference regarding security. Security Director from Harvard Art Museum will be visiting UConn for security assessment. Nancy has Melissa Frank (legal) liaison UConn’s policy doesn’t include art insurance. Divided by exhibit & permanent. (Within Hartford insurance umbrella) | Per C. Bridgeman - mitiation strategy in place. | Per C. Bridgeman - mitiation strategy in place. | Per C. Bridgeman - mitiation strategy in place.
7 | IPE |  | Steam Shutdown Initiative- occurring during the May timeframe and is there a mitigation plan? |  |  | FacOps has the shutdown scheduled and plan to prevent damage to collection | Add 2 heaters to prepare. Can put under complete
6 | IPE | Benton Gallery | Replacement carpet to hard wood or composite |  |  | Summer 2017 – Pete will be getting a quote | Meeting is scheduled with Pete Dunnack and Benton team to discuss options and evaluate needs on 11/2/17. 2 or 3 galleries. Center and East gallery, East Gallery concerned about sound mitigation | Completed; closed-out. | N/A | N/A
7 | S | East Gallery | Exit Doors |  |  |  | Fire Marshall established that one of the exit doors in the East Gallery is unnecessary and they’re going to remove the exit. | Completed; closed-out. | N/A | N/A
8 |  | Benton Museum | Access to rooms for facilities or UITS |  |  |  | Nancy wants to limit access to all rooms within the Benton to 3 staff members. Anyone who wants access will have to go through the 3 staff members, except in emergencies. Dean's office requesting keys to be included in master set. | Completed; closed-out. | N/A | N/A
9 | IPE | Benton Museum | There are humidity and temperature requirements for installations. On 11/15, the humidity and temperature dropped drastically and 3 HVAC Units were non-operational. Requesting some sort of alarm system when humidity/temperature/HVAC failures occur. | [5 empty] | Seems to have stabilized, however, this issue still needs to be addresses for further occurrences. | OK; complete Follow-up meeting occurred with Glen Mathieu, Peter McQueeney and Benton Staff; conclusion was to institute a Standard Operating procedure for future remediation of HVAC issues to better maintain and preserve the museum’s collection. Benton developed and disseminated to Facilities Operations 03/07/19.
10 | S | Benton Museum | Shares a space with The Beanery Coffee Shop and the Benton Bathrooms are used by their patrons. However, they are also taking over the front desk area and the sculpture atrium when the Museum is closed. They would like to close the gate between the shop and museum when museum is closed, however, that would required The Beanery to acquire their own restrooms. | [5 empty] | It was suggested to add signage in the Interim and Colleen encourages to speak about this further offline. Facilities has suggested a Project Request to get started on the conversation of new, separate restroom facilities. | CKB to follow up with Anne

## BIMP
Ballard Institute & Museum of Puppetry
Rank | Priority | Area/Building/Room# | Issue | As of 10/6/2016 | As of 3/23/2017 | As of 3/27/2017 | As of 10/20/17 | SFA/Facilities Update as of 11/01/18 | SFA Facility Issues as of 11/16/2018 | SFA Facilities Update as of 04/18/2019 | Progress
1 | S | Exterior Doors | Keyswipe change for locks | Emily has been working with facilities to resolve keyswipe issues. |  | Has been addressed and should be all set | Key swipe system continues to be problematic. Before 9 am students have issues with access. Schedule meeting with Dana in early AM to test. Could it be an issue with time change? | Unresolved; need update from BIMP/Facilities | Unresolved; need update from BIMP/Facilities | Unresolved; need update from BIMP/Facilities
2 | IPE | Exhibit Cases | Humidity control can be resolved from a "Nest" unit | Eric Kruger is going to see if they can split the humidity control into two zones | Part arrived from NY – improving daily Cannot split humidifier units. Overall humidity has improved, and w/o’s placed have maintained control in system | He wants someone there to put it – Pete Dunnach Emily with FME transport costumes | Complete
2 | IPE | Willimantic, Mansfield & Bolton Cottages | Storage, Temperature Control concerns for collections. Data loggers at Depot to see what the humidity and temperature is like, and then we can see if a humidity system is necessary | Long term solution needs further discussion to address improved climate control, better facility monitoring and adequate space for incoming donated collections. |  | Can be resolved from a “Nest” unit Eric Kruger – order nest units to monitor humidity control | Eric Krueger is unsure if they Installed alarm to test temperature or industrial monitor. Nest units are really for domestic areas. Enter WO | Unresolved; need update from Facilities. Update 11/01/18: C. Bridgeman working with UPDC on alternative storage locations more suitable for collections storage. | Unresolved; need update from Facilities. Update 11/01/18: C. Bridgeman working with UPDC on alternative storage locations more suitable for collections storage. | Unresolved; need update from Facilities. Update 11/01/18: C. Bridgeman working with UPDC on alternative storage locations more suitable for collections storage.
4 |  | Mansfield | Rodent Issues (moths/mice) | Topic arose as discussion of Depot arose. Facilities recommended calling Waltham. Carissa submitted WO—Waltham called to explain that there are not treatments for clothes moths. Suggested purchasing pheromone traps to contain them or place affected clothes in freezer. Waltham rep has been in touch with Emily W. and explained limits of treatments. Carissa will touch base with Emily to confirm purchase of pheromone traps. |  |  | Complete
5 |  | Ashford | Access-keys have been changed. Puppet Arts collections remain in Ashford | Recommended to contact locksmith to gain access to transition collection out of Ashford. |  | E. Richs will follow up w/ Bart regarding Puppet Arts items within building | Complete
3 | IPE, A | Ballard Institute |  |  |  |  | Plumbing issues in bathrooms-forced to shut down and close bathrooms continually. This is probably a design issue. Eric k will delegate work to Mike Rocchetti, FacOps mechanical engineer, to address. Handicap men's and women's not paper towels, external to building. Meeting with Barnes & noble team to manage access. | Unresolved; need update from BIMP/Facilities | Unresolved; need meeting with Barnes & Noble to readdress operating procedures with respect to bathroom usage. Emily setting up meeting w/ B&N, CKB and Facilities to address continuous issues and concerns. | Unresolved; need meeting with Barnes & Noble to readdress operating procedures with respect to bathroom usage. Emily setting up meeting w/ B&N, CKB and Facilities to address continuous issues and concerns.
4 |  | Security Cameras |  |  |  |  | Barnes & Noble take cameras off same unit as BIMP. Piggyback off of Benton's meeting with Harvard Security. Colleen and Emily will meet with them afterwards. Will follow up with sales manager from B&N-break away from their system | Unresolved; need update from Facilities. | Unresolved; need update from BIMP/Public Safety | Unresolved; need update from BIMP/Public Safety
5 |  | Emergency Exits |  |  |  |  | Exit keeps blinking - faulty wiring? Emily has entered two WO'S for them | Unresolved; need update from Facilities. | Unresolved; need update from BIMP/Facilities | Unresolved; need update from BIMP/Facilities
6 |  | Merritt Cottage |  |  |  |  | Bart needs access for storage | Completed; closed-out. | N/A | N/A
7 | S | BIMP | Needs change-over to Uconn system security camera | [5 empty] | He is going to try to get a vendor in over the next few weeks to determine if new cameras are needed or if the existing cameras can be reconfigured. Detective Hanna is creating a report. | Work has been done on the security system in last couple of weeks, no confirmation as to whether it is officially on the UConn system. Emily to follow-up.
8 | HSIPE | Depot Buildings; Willimantic and Bolton | Ongoing issue with mice in these spaces; poison traps have been set. | [5 empty] | Place work orders to replace poison traps and place work order every time an occurrence happens. | BIMP continues to monitor the mouse traps. Exterminator recommended putting traps around the perimeter of the exterior of the building, but that work is outside his contract with UConn. Jay will contact Billy from Waltham to see of this is possible. Outside traps have been typically banned due to protected species policy.
9 | A | BIMP Restrooms | Hardware and hinges on restroom stalls need to be checked as temporary hinges are not working properly. | [5 empty] | Work order has been placed for this New Item. Facilities to follow-up | Jay will touch base with Carpentry--hinges do take a while to order.
10 | IPE | Bimp Lobby and Gallery | Ceiling Panels in the lobby and gallery are water-damaged and need to be replaced. | [5 empty] | Working with Carpentry and replacement should occur within the next week or so. | OK; Complete as per Emily Wicks
11 | IPE | BIMP Museum Space | Fan is not working. | [5 empty] | New Item; work order placed. | OK; Complete per Emily Wicks
12 | IPE | BIMP Vestibule | HVAC/Humidity control continues to be an issue. | [5 empty] | A alarm system has been requested to let the staff know when the HVAC goes out so they may place work orders. Facilities will follow up on this issue. | April 10 - Productive meeting with Mike Rocchetti and Newman Architects to review Ballard HVAC issues. Newman to conduct a site visit to evaluate space; recommend HVAC consultant with museum preservation experience and include plans for remediation with their proposal; expected in about 3 weeks.
13 | IPE | BIMP Restrooms | General cleanliness; shares a cleaning crew with B&N who are reportedly un-reliable. BIMP is requesting UConn Facilities take over the space. | [5 empty] | Facilities is encouraging BIMP to check their lease and see what is required of the cleaning crew. First step is to hold the contracted party accountable and Facilities is willing to lend a hand in this area. The suggestion was also made to limit who uses the restrooms via master key. | BIMP still having cleanliness issues. They met with the new manager of the cleaning company, and he said he would work with Len and us to create a clear list of items to be done. Issues are unresolved. Emily to schedule meeting w/ B&N, CKB and Facilities to address cleaning issues and develop standard operating procedures.